## Summary
Description | UOM | Value | Actual Load KVA | Remarks
Service-1 Utility Sanction Load KVA | KVA | 4000 | 2798
Service-2 Utility Sanction Load KVA | KVA | 0 | 0
Customer contracted capacity | KVA

## NEW SUMMARY
POWER SUMMARY | Contract Demand | Utility Consump | Demand % | IT Consump | PUE
Bangalore EB Service-1 | 4000 | 2798 | 69.95%
| 0 | 0 | #DIV/0!
TOTAL Bangalore-01 | 4000 | 2798 | 69.95% | 1574 | 1.7776
INVENTORY SUMMARY | IT KW CAPACITY |  |  | IT KW CONSUMPTION |  | RACKSPACE CAPACITY
| Design | Sold | Available | Consumed | % of Sold | Design | Des - Losses | Sold | Available
TOTAL Bangalore-01 | 4860 | 2891 | 1969 | 2124.6 | 73.49% | 925 | 2153 | 720 | 137
BNG 01 by Floor:
L1 | 540 | 305 | 235 | 91.5 | 30% | 130 | 82 | 63 | 19
L3 | 1620 | 1566 | 54 | 1075.4 | 68.67% | 540 | 520 | 402 | 118
L2 | 1080 | 1020 | 60 | 957.7 | 93.89% | 255 | 255 | 255 | 0

## Facility details
Description | Value | Actual Load KVA
| As per the Sanction Letter | Usage measured on 1of every month
Utility Sanction Load KVA | 4000 kVA | 2573
Utility Minimum Demand % | 100 | 64.33%
Utility Sanction Load KVA | 0 | 0 | [18 empty] | 13503
Utility Minimum Demand % | 0 | 0
Capacity Installed | Transformer kW | No of TX | Catcher TX kW | No. Of catcher | Actual Load kW | Generator kW | No of DG | Catcher DG kW | No. Of catcher | UPS kW | UPS Config | IT capacity Installed kW | IT Power Sold in kW ( considering unity as PF) | Allocated IT Power to customer ( Taking 50% as divercity factor for rated power customer ) | IT kW Usage | Avaialble IT kW Design-Used | Available IT kW Design-Sold | Available IT kW Design-Sold ( Allocated capacity) | MAX Rack Capacity | Rack Space sold out | Rack losss ( Cage+ non standard rack+ path) | Available space | Designed White Space ( in SQ FT) | Used White Space( in SQ FT) | Avaialble White Space ( in SQ FT)
| Mention the design kW capacity of Transformer |  |  |  |  | Mention the design kW capacity of Generator |  |  |  | Mention the design N capacity in kw in a N+N Configuration |  | Installed including interfloor shared capacity | Customer subscribed IT kW | Allocated power | Measured on 1st of every month | Measured on 1st of every month | Measured on 1st of every month | Measured on 1st of every month
L1 | 1600 | 1 | 1600 | 1 | 135.5 | 1600 | 1 | 1600 | 1 | 540 | 300kVA X 2 No’s – Source A 300kVA X 2 no’s- Source B | 540 | 305 | 305 | 91.5 | 448.5 | 235 | 235 | 130 | 63 | 48 | 19 | 3300 | 2857 | 443
L3 | 1600 | 1 |  |  | 1460 | 1600 | 1 |  |  | 1620 | 600kVA X 3 No’s – Source A 600kVA X 3 no’s- Source B | 1620 | 2106.5 | 1566 | 1075.4 | 544.6 | -486.5 | 54 | 540 | 402 | 20 | 118 | 13820 | 9844 | 3976
L2 | 1800 | 1 | 1800 | 1 | 823 | 1800 | 1 | 1800 | 1 | 1080 | 600kVA X 2 No’s – Source A 600kVA X 2 no’s- Source B | 1080 | 1020 | 1020 | 957.7 | 122.3 | 60 | 60 | 255 | 255 | 0 | 0 | 6120 | 6120 | 0
Total | [9 empty] | 3240 |  | 3240 | 3431.5 | 2891 | 2124.6 | 1115.4 | -191.5 | 349 | 925 | 720 | 68 | 137 | 23240 | 18821 | 4419
Note on V11: Customer cage has been lost due to power module with high density racks

## Customer details
Floor | Floor / Module | Customer Name | RHS/SH | Power Subscription Model (Rated/Subscribed) | Power Usage Model (Bundled / Metered) | Subscription Mode | Caged /Uncaged | UoM | Subscription | In Use | Yet to be given/ | Billed | Reserved Capacity if any (Non-Billable) | Per Unit rate (MRC) | Subscription Model | UoM | Total Capacity Purchased | Capacity in Use | Capacity to be given | Reserved Capacity if any | Subscribed Capacity to be given in KW | "Allocated" Capacity in KW | DC NW Infra | Usage in KW | Billable Additional Capacity | Additional Capacity Charges (MRC) | Usage Model | Multiplier | Unit rate Model (Fixed/Variable) | Unit Rate (per KW-HR) | No Of Units (KW-HR/ Month | Subscription Model | UoM | Subscription | In Use | Yet to be given | Billed | Reserved Capacity if any | Per Unit rate | Space revenue including capacity | Additional Capacity Revenue | Power Usage revenue | Seating Space | Any Other Items | Total Revenue | Billing Frequency | Sales Order ref No | Contract Start Date | Term of Contract (No of Years) | Current Expiry Date | Remarks if any | Cross connect
L1 | L1 | Axis bank | No | Subscribed | Metered | Rack | Caged | No of Racks | 50 | 50 | 0 | 50 | 0 | 26333.3333 | Subscribed | kVA | 305 | 63.6392 | 241.3608 | 0 | 241.3608 | 305 | 63.6392 | 63.6392 | -241.3608 |  | Metered | 1.6 | Variable |  | 42765.55 | No of Seats | No of seats | 5 | 5 | 0 | 5 | 0 |  | 1316666.6667 |  | 0 | 0 |  | 1316666.6667
L2 | L2 | Union Bank | No | Subscribed | Metered | Rack | Caged | No of Racks | 255 | 255 | 0 | 255 | 0 | 30153.3333 | Subscribed | KVA | 1020 | 530.0311 | 489.9689 | 0 | 489.9689 | 1020 | 530.0311 | 530.0311 | -489.9689 |  | Metered | 1.75 | Fixed |  | 356180.91 | No of Seats | No of seats | 28 | 28 | 0 | 28 | 0 | 4112 | 7689100 |  | 0 | 115136 | 875306 | 8679542
L3 | DC-3 | Yes bank | No | Subscribed | Metered | Rack | Caged | No of Racks | 55 | 55 | 0 | 55 | 0 | 38896 | Subscribed | KVA | 452 | 173.0791 | 278.9209 | 0 | 278.9209 | 452 | 173.0791 | 173.0791 | -278.9209 |  | Metered | 1.8 |  |  | 116309.14 | No of Seats | No of seats | 8 | 8 | 0 | 8 | 0 |  | 2139280 |  | 0 | 0 |  | 2139280
L3 | DC-3 | UST Global | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 5 | 5 | 0 | 5 | 0 | 20543.7333 | Subscribed | KVA | 45 | 17.0582 | 27.9418 | 0 | 27.9418 | 45 | 17.0582 | 17.0582 | -27.9418 |  | Metered | 1.8 |  |  | 11463.1 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 102718.6667 |  | 0 | 0 |  | 102718.6667
L3 | DC-3 | Data vision software solutions pvt ltd | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 12 | 11.61 | 0.39 | 0 | #REF! | #REF! | 11.61 | 11.61 | -0.39 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0
L3 | DC-2 | The Oriental Insurance Company Limited | No | Subscribed | Metered | Space | Caged | Sq Ft | 600 | 600 | 0 | 600 | 0 | 736 | Subscribed | KVA | 60 | 58.0633 | 1.9367 | 0 | 1.9367 | 60 | 58.0633 | 58.0633 | -1.9367 |  | Metered | 1.8 |  |  | 39018.53 | No of Seats | No of seats | 10 | 10 | 0 | 10 | 0 |  | 441600 |  | 0 | 0 |  | 441600
L3 | DC-2 | AGRICULTURE INSURANCE COMPANY OF INDIA LIMITED | No | Subscribed | Metered | Rack | Uncaged | No of Racks | 14 | 14 | 0 | 14 | 0 | 13333.3333 | Subscribed | KVA | 102.5 | 26.2497 | 76.2503 | 0 | 76.2503 | 102.5 | 26.2497 | 26.2497 | -76.2503 |  | Metered | 1.8 |  |  | 17639.83 | No of Seats | No of seats | 3 | 3 | 0 | 3 | 0 |  | 186666.6667 |  | 0 | 0 |  | 186666.6667
L3 | DC-2 | Polestar | No | Subscribed | Metered | Rack | Caged | No of Racks | 5 | 5 | 0 | 5 | 0 | 46250 | Subscribed | KVA | 12.5 | 10.3356 | 2.1644 | 0 | 2.1644 | 12.5 | 10.3356 | 10.3356 | -2.1644 | 6666.6667 | Metered | 1.8 |  |  | 6945.51 | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0 |  | 231250 |  | 0 | 0 |  | 231250
L3 | DC-2 | New India Assurance Co. Ltd. | No | Subscribed | Metered | Rack | Caged | No of Racks | 18 | 18 | 0 | 18 | 0 | 14814.8333 | Subscribed | KVA | 88 | 68.0016 | 19.9984 | 0 | 19.9984 | 88 | 68.0016 | 68.0016 | -19.9984 |  | Metered | 1.8 |  |  | 45697.05 | No of Seats | No of seats | 3 | 3 | 0 | 3 | 0 |  | 266667 |  | 0 | 0 |  | 266667
L3 | DC-2 | Torrent Power | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 4 | 4 | 0 | 4 | 0 | 32333.3333 | Subscribed | KVA | 19 | 13.321 | 5.679 | 0 | 5.679 | 19 | 13.321 | 13.321 | -5.679 |  | Metered | 1.8 |  |  | 8951.68 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 129333.3333 |  | 0 | 0 |  | 129333.3333
L3 | DC-2 | LIC HOUSING FINANCE LTD | yes | Subscribed | Metered | Rack | Caged | No of Racks | 10 | 10 | 0 | 10 | 0 | 37370.125 | Subscribed | KVA | 30 | 13.0921 | 16.9079 | 0 | 16.9079 | 30 | 13.0921 | 13.0921 | -16.9079 |  | Metered | 1.8 |  |  | 8797.9 | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0 |  | 373701.25 |  | 0 | 0 |  | 373701.25
L3 | DC-2 | Avenue Supermart (Dmart) | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 10 | 10 | 0 | 10 | 0 | 46805.6389 | Rated | KVA | 83 | 72.47 | 10.53 | 0 | #REF! | #REF! | 72.47 | 72.47 | -10.53 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 468056.3889 |  | 0 | 0 |  | 468056.3889
L3 | DC-2 | Aviva | No | Rated | Bundled | Rack | Caged | No of Racks | 6 | 6 | 0 | 6 | 0 | 57128.75 | Rated | KVA | 36 | 23.46 | 12.54 | 0 | #REF! | #REF! | 23.46 | 23.46 | -12.54 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0 |  | 342772.5 |  | 0 | 0 |  | 342772.5
L3 | DC-2 | HITPA | yes | Rated | Bundled | Rack | Caged | No of Racks | 7 | 7 | 0 | 7 | 0 | 55000 | Rated | KVA | 45 | 23.18 | 21.82 | 0 | #REF! | #REF! | 23.18 | 23.18 | -21.82 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 385000 |  | 0 | 0 |  | 385000
L3 | DC-2 | Stock holding corporation of India | No | Subscribed | Metered | Rack | Caged | No of Racks | 13 | 13 | 0 | 13 | 0 | 49915.9167 | Subscribed | KW | 42 | 23.7682 | 18.2318 | 0 | 18.2318 | 42 | 23.7682 | 23.7682 | -18.2318 |  | Metered | 1.8 |  |  | 15972.2 | No of Seats | No of seats | 5 | 5 | 0 | 5 | 0 |  | 648906.9167 |  | 0 | 0 |  | 648906.9167
L3 | DC-2 | SIMPLE TELECOM PVT LTD | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 17500 | Subscribed | KW | 2.5 | 0.84167 | 1.6583 | 0 | 1.6583 | 2.5 | 0.84167 | 0.84167 | -1.6583 |  | Metered | 1.8 |  |  | 565.6 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 17500 |  | 0 | 0 |  | 17500
L3 | DC-1 | Vishal Megamart | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 8 | 8 | 0 | 8 | 0 | 17708.3333 | Subscribed | KW | 32.5 | 27.6982 | 4.8018 | 0 | 4.8018 | 32.5 | 27.6982 | 27.6982 | -4.8018 |  | Metered | 1.8 |  |  | 18613.19 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 141666.6667 |  | 0 | 0 |  | 141666.6667
L3 | DC-1 | MEIKO CLEAN SOLUTIONS (INDIA) PRIVATE LIMITED | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Subscribed | KVA | 3 | 2.2065 | 0.79347 | 0 | 0.79347 | 3 | 2.2065 | 2.2065 | -0.79347 |  | Metered | 1.8 |  |  | 1482.79 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0
L3 | DC-1 | CONTAQUE CLOUD PVT LTD | yes | Rated | Bundled | U space | Uncaged | U Space | 21 | 21 | 0 | 21 | 0 |  | Rated | KW | 4 | 4.29 | -0.29 | 0 | 0 | #REF! | 4.29 | 4.29 | 0.29 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0
L3 | DC-1 | CONTAQUE CLOUD PVT LTD | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Subscribed | KW | 3 | 1.8182 | 1.1818 | 0 | 1.1818 | 3 | 1.8182 | 1.8182 | -1.1818 |  | Metered | 1.8 |  |  | 1221.83 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0
L3 | DC-1 | CLINISYS INDIA PRIVATE LIMITED | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Subscribed | KW | 7 | 4.9217 | 2.0783 | 0 | 2.0783 | 7 | 4.9217 | 4.9217 | -2.0783 |  | Metered | 1.8 |  |  | 3307.37 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0
L3 | DC-1 | BAJAJ FINANCE LTD | No | Subscribed | Metered | Rack | Caged | No of Racks | 5 | 5 | 0 | 5 | 0 | 1019.75 | Subscribed | KVA | 30 | 16.4925 | 13.5075 | 0 | 13.5075 | 30 | 16.4925 | 16.4925 | -13.5075 |  | Metered | 1.8 |  |  | 11082.97 | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0 |  | 5098.75 |  | 0 | 0 |  | 5098.75
L3 | DC-1 | UNISYS INDIA PVT LTD | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 41250 | Rated | KVA | 6 | 5.5 | 0.5 | 0 | #REF! | #REF! | 5.5 | 5.5 | -0.5 | 8333.3333 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 41250 |  | 0 | 0 |  | 41250
L3 | DC-1 | Hindustan Pencil | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 94791.6667 | Rated | KVA | 5.83 | 5.8 | 0.03 | 0 | #REF! | #REF! | 5.8 | 5.8 | -0.03 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 94791.6667 |  | 0 | 0 |  | 94791.6667
L3 | DC-1 | J2 Global | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 46979.1667 | Rated | KVA | 3 | 4.78 | -1.78 | 0 | 0 | #REF! | 4.78 | 4.78 | 1.78 | 9166.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 46979.1667 |  | 0 | 0 |  | 46979.1667
L3 | DC-1 | Ubona | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 54162.5 | Rated | KVA | 12 | 11.14 | 0.86 | 0 | #REF! | #REF! | 11.14 | 11.14 | -0.86 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 54162.5 |  | 0 | 0 |  | 54162.5
L3 | DC-1 | Ramco | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 | 3375 | Rated | KVA | 12 | 11.85 | 0.15 | 0 | #REF! | #REF! | 11.85 | 11.85 | -0.15 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 6750 |  | 0 | 0 |  | 6750
L3 | DC-1 | Sixth Energy (NEUREOL) | Yes | Rated | Bundled | U space | Uncaged | U Space | 37 | 27 | 10 | 37 | 0 | 86429.7083 | Rated | KVA | 14.94 | 14.94 | 0 | 0 | 0 | #REF! | 14.94 | 14.94 | 0 | 9166.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 3197899.2083 |  | 0 | 0 |  | 3197899.2083
L3 | DC-1 | Kluber | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 55004.1667 | Rated | KVA | 12 | 11.92 | 0.08 | 0 | #REF! | #REF! | 11.92 | 11.92 | -0.08 | 6666.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 55004.1667 |  | 0 | 0 |  | 55004.1667
L3 | DC-1 | Ozonetel | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 11 | 11 | 0 | 11 | 0 | 46761 | Rated | KVA | 115.5 | 118.33 | -2.83 | 0 | 0 | #REF! | 118.33 | 118.33 | 2.83 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 514371 |  | 0 | 0 |  | 514371
L3 | DC-1 | SingTel | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 4 | 4 | 0 | 4 | 0 | 50833.3333 | Rated | KVA | 12 | 7.28 | 4.72 | 0 | #REF! | #REF! | 7.28 | 7.28 | -4.72 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 203333.3333 |  | 0 | 0 |  | 203333.3333
L3 | DC-1 | Thane Cooperative Bank | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 | 40833.3333 | Rated | KVA | 10 | 9.27 | 0.73 | 0 | #REF! | #REF! | 9.27 | 9.27 | -0.73 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 81666.6667 |  | 0 | 0 |  | 81666.6667
L3 | DC-1 | Knowlarity | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 7 | 7 | 0 | 7 | 0 | 41500 | Rated | KVA | 48.53 | 47.9 | 0.63 | 0 | #REF! | #REF! | 47.9 | 47.9 | -0.63 | 9166.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 290500 |  | 0 | 0 |  | 290500
L3 | DC-1 | Gradatim | Yes | Rated | Bundled | U space | Uncaged | U Space | 9 | 9 | 0 | 9 | 0 | 2666.6667 | Rated | KVA | 8.06 | 3.9 | 4.16 | 0 | #REF! | #REF! | 3.9 | 3.9 | -4.16 | 0 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 24000 |  | 0 | 0 |  | 24000
L3 | DC-1 | INFIBEAM AVENUES LIMITED | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 | 36479.1667 | Rated | KVA | 21 | 23.3 | -2.3 | 0 | 0 | #REF! | 23.3 | 23.3 | 2.3 | 7083.3333 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 72958.3333 |  | 0 | 0 |  | 72958.3333
L3 | DC-1 | Maximus Infoware | Yes | Rated | Bundled | U space | Uncaged | U Space | 8 | 5 | 3 | 8 | 0 | 45833.3333 | Rated | KVA | 1.75 | 1.6 | 0.15 | 0 | #REF! | #REF! | 1.6 | 1.6 | -0.15 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Avenue Ecommerce | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 4 | 4 | 0 | 4 | 0 | 50000 | Rated | KVA | 33 | 28.03 | 4.97 | 0 | #REF! | #REF! | 28.03 | 28.03 | -4.97 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | ESAB | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 22256.3333 | Rated | KVA | 9 | 2.9 | 6.1 | 0 | #REF! | #REF! | 2.9 | 2.9 | -6.1 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | INSURANCE INFORMATION BUREAU OF INDIA | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 3 | 3 | 0 | 3 | 0 | 35066.6667 | Rated | KVA | 37.5 | 9.82 | 27.68 | 0 | #REF! | #REF! | 9.82 | 9.82 | -27.68 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | NIXI | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 5833.3333 | Rated | KVA | 3.5 | 2.84 | 0.66 | 0 | #REF! | #REF! | 2.84 | 2.84 | -0.66 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | UPPCL | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 0 | Rated | KVA | 6 | 8.02 | -2.02 | 0 | 0 | #REF! | 8.02 | 8.02 | 2.02 | 0 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Max Bhupa | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 33333.3333 | Rated | KVA | 3 | 3.97 | -0.97 | 0 | 0 | #REF! | 3.97 | 3.97 | 0.97 | 0 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | L&T infotech | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 | 45833.3333 | Rated | KVA | 9 | 4.91 | 4.09 | 0 | #REF! | #REF! | 4.91 | 4.91 | -4.09 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Hughes Communications | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 40000 | Rated | KVA | 3 | 1.64 | 1.36 | 0 | #REF! | #REF! | 1.64 | 1.64 | -1.36 | 8166.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Jubilant Motors | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 4 | 3 | 1 | 4 | 0 | 1170.6349 | Rated | KVA | 1 | 0.44 | 0.56 | 0 | #REF! | #REF! | 0.44 | 0.44 | -0.56 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | GIC | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 45000 | Rated | KVA | 6 | 5.52 | 0.48 | 0 | #REF! | #REF! | 5.52 | 5.52 | -0.48 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Happiest Mind | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 40416.6667 | Rated | KVA | 3 | 1.98 | 1.02 | 0 | #REF! | #REF! | 1.98 | 1.98 | -1.02 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Bajoria | Yes | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 | 0 | 65416.6667 | Rated | KVA | 0.5 | 0.27 | 0.23 | 0 | #REF! | #REF! | 0.27 | 0.27 | -0.23 | 7916.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | ACT Broad band | Yes | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 | 0 | 70000 | Rated | KVA | 0.25 | 0.22 | 0.03 | 0 | #REF! | #REF! | 0.22 | 0.22 | -0.03 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Aspiration Images | Yes | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 | 0 | 3083.3333 | Rated | KVA | 0.25 | 0.233 | 0.017 | 0 | #REF! | #REF! | 0.233 | 0.233 | -0.017 | 7083.3333 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Vashi Electricals | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 21 | 21 | 0 | 21 | 0 | 2916.6667 | Rated | KVA | 4 | 3.93 | 0.07 | 0 | #REF! | #REF! | 3.93 | 3.93 | -0.07 | 7083.3333 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | TCI Express | Yes | Rated | Bundled | U space | Uncaged | U Space | 4 | 6 | -2 | 4 | 0 | 857.1429 | Rated | KVA | 1 | 2.11 | -1.11 | 0 | 0 | #REF! | 2.11 | 2.11 | 1.11 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | PRAMERICA LIFE INSURANCE LIMITED | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 3 | 3 | 0 | 3 | 0 | 2916.6667 | Rated | KVA | 16 | 16.16 | -0.16 | 0 | 0 | #REF! | 16.16 | 16.16 | 0.16 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | NISM | Yes | Rated | Bundled | U space | Uncaged | U Space | 4 | 4 | 0 | 4 | 0 | 57279.1667 | Rated | KVA | 1.72 | 1.4 | 0.32 | 0 | #REF! | #REF! | 1.4 | 1.4 | -0.32 | 7916.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Wildcraft | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 4140.625 | Rated | KVA | 9.5 | 10.53 | -1.03 | 0 | 0 | #REF! | 10.53 | 10.53 | 1.03 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Bombay Merchantile Co Operative Bank Ltd IFTAS | Yes | Rated | Bundled | U space | Uncaged | U Space | 4 | 4 | 0 | 4 | 0 | 1666.6667 | Rated | KVA | 1 | 0.505 | 0.495 | 0 | #REF! | #REF! | 0.505 | 0.505 | -0.495 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Triveni Engineering | Yes | Rated | Bundled | U space | Uncaged | U Space | 21 | 21 | 0 | 21 | 0 |  | Rated | KVA | 1.5 | 1.44 | 0.06 | 0 | #REF! | #REF! | 1.44 | 1.44 | -0.06 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Coforge Ltd | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 8 | 7.28 | 0.72 | 0 | #REF! | #REF! | 7.28 | 7.28 | -0.72 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | United brewaries LTD | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Rated | KVA | 22 | 22.87 | -0.87 | 0 | 0 | #REF! | 22.87 | 22.87 | 0.87 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | DBFS Securities Limited | Yes | Rated | Bundled | U space | Uncaged | U Space | 3 | 3 | 0 | 3 | 0 |  | Rated | KVA | 0.75 | 0.366 | 0.384 | 0 | #REF! | #REF! | 0.366 | 0.366 | -0.384 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | TELECMI Technologies | Yes | Rated | Bundled | U space | Uncaged | U Space | 3 | 2 | 1 | 3 | 0 |  | Rated | KVA | 1 | 0.833 | 0.167 | 0 | #REF! | #REF! | 0.833 | 0.833 | -0.167 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-2 | Extreme | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 3 | 0.711 | 2.289 | 0 | #REF! | #REF! | 0.711 | 0.711 | -2.289 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Kansai Nerolac | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 6.25 | 5.83 | 0.42 | 0 | #REF! | #REF! | 5.83 | 5.83 | -0.42 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | ISHAN | Yes | Rated | Bundled | U space | Uncaged | U Space | 2 | 2 | 0 | 2 | 0 |  | Rated | KVA | 0.5 | 0.138 | 0.362 | 0 | #REF! | #REF! | 0.138 | 0.138 | -0.362 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Jiffy (SRI LAKSHMI NETWORKS PRIVATE LIMITED) | Yes | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 0.25 | 0.26 | -0.01 | 0 | 0 | #REF! | 0.26 | 0.26 | 0.01 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Tech Solve Engine | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Rated | KVA | 12 | 11.4 | 0.6 | 0 | #REF! | #REF! | 11.4 | 11.4 | -0.6 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | MMR-4 | LIGHTSTORM TELECOM CONNECTIVITY PRIVATE LIMITED | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Rated | KVA | 8 | 4.01 | 3.99 | 0 | #REF! | #REF! | 4.01 | 4.01 | -3.99 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | IFB INDUSTRIES LIMITED | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 4 | 4 | 0 | 4 | 0 |  | Rated | KVA | 24 | 36.8 | -12.8 | 0 | 0 | #REF! | 36.8 | 36.8 | 12.8 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | CHEMPLAST SANMAR LTD | Yes | Rated | Bundled | U space | Uncaged | U Space | 21 | 1 | 20 | 21 | 0 |  | Rated | KVA | 1.75 | 0.17 | 1.58 | 0 | #REF! | #REF! | 0.17 | 0.17 | -1.58 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | MN WORLD ENTERPRISE PVT LTD | Yes | Rated | Bundled | U space | Uncaged | U Space | 4 | 3 | 1 | 4 | 0 |  | Rated | KVA | 1 | 0.608 | 0.392 | 0 | #REF! | #REF! | 0.608 | 0.608 | -0.392 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | SITA INC INDIA PVT LTD | Yes | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 | 0 | 1170.6349 | Rated | KVA | 0.25 | 0.033 | 0.217 | 0 | #REF! | #REF! | 0.033 | 0.033 | -0.217 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | ACCUPAYD TECH PRIVATE LIMITED | Yes | Rated | Bundled | U space | Uncaged | U Space | 12 | 8 | 4 | 12 | 0 |  | Rated | KVA | 2.5 | 1.3 | 1.2 | 0 | #REF! | #REF! | 1.3 | 1.3 | -1.2 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | HITACHI ASTEMO GURUGRAM POWERTRAIN SYSTEMS PRIVATE LIMITED | yes | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 0.25 | 0.022 | 0.228 | 0 | #REF! | #REF! | 0.022 | 0.022 | -0.228 | 7500 | Rated | 1.8 |  |  |  | No of Seats | no of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | Cloud project 1 * 2 | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 46 | 46 | 0 | 46 | 0 |  | Rated | KVA | 200 | 153.032 | 46.968 | 0 | #REF! | #REF! | 153.032 | 153.032 | -46.968 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0
L3 | DC-1 | Managed services project | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 7 | 7 | 0 | 7 | 0 | 40833.3333 | Rated | KVA | 42 | 40.87 | 1.13 | 0 | #REF! | #REF! | 40.87 | 40.87 | -1.13 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | NOC | NOC | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 14 | 14 | 0 | 14 | 0 | 40833.3333 | Rated | KVA | 20 | 39.9 | -19.9 | 0 | 0 | #REF! | 39.9 | 39.9 | 19.9 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0
L3 | DC-2 | ESAF SMALL FINANCE BANK LIMITED | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 13 | 13 | 0 | 13 | 0 |  | Subscribed | KVA | 72.5 | 44.7395 | 27.7605 | 0 | 27.7605 | 72.5 | 44.7395 | 44.7395 | -27.7605 |  | Metered | 1.8 |  |  | 30064.93 | No of Seats | No of seats | 6 | 6 | 0 | 6 | 0 | [8 empty] | 521007266 | 2025-03-12
L3 | DC-1 | MANGALORE REFINERY AND PETROCHEMICALS LTD | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Rated | KVA | 12 | 6.98 | 5.02 | 0 | #REF! | #REF! | 6.98 | 6.98 | -5.02 |  | Metered | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 | [8 empty] | 521007213 | 2025-03-10
L3 | DC-1 | SHIVTEL COMMUNICATIONS PRIVATE LIMITED | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Subscribed | KW | 3 | 3.5172 | -0.51716 | 0 | 0 | 3 | 3.5172 | 3.5172 | 0.51716 |  | Metered |  |  |  | 2363.53 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | TCI SUPPLY CHAIN SOLUTION A DIVISION OF TRANSPORT | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 4 | 3.844 | 0.156 | 0 | #REF! | #REF! | 3.844 | 3.844 | -0.156 |  | Rated |  |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | MAXIMUS INFOWARE(INDIA) PVT LTD | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 6 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | -6 |  | Rated |  |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | ISHAN NETSOL PVT LTD | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 6 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | -6 |  | Rated |  |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | AAPTTEKNOUS SERVICES PRIVATE LIMITED | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 5 | 5 | 0 | 5 | 0 |  | Subscribed | KW | 15 | 1.9682 | 13.0318 | 0 | 13.0318 | 15 | 1.9682 | 1.9682 | -13.0318 |  | Metered |  |  |  | 1322.62 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | ALTIMAT DATA CENTER INDIA PRIVATE LIMITED | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Subscribed | KW | 7 | 0 | 7 | 0 | 7 | 7 | 0 | 0 | -7 |  | Metered |  |  |  | 0 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | INFRASOFT TECHNOLOGIES LIMITIED | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Rated | KVA | 12 | 0 | 12 | 0 | 12 | 0 | 0 | 0 | -12 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | KARNATAKA FASTNET PRIVATE LIMITED | yes | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 0.25 | 0.2 | 0.05 | 0 | #REF! | #REF! | 0.2 | 0.2 | -0.05 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 | [8 empty] | 521008118
L3 | DC-1 | CARE RATINGS LIMITED | yes | Rated | Bundled | U space | Uncaged | U Space | 21 | 21 | 0 | 21 | 0 |  | Rated | KVA | 3 | 2.41 | 0.59 | 0 | #REF! | #REF! | 2.41 | 2.41 | -0.59 | 7500 | Rated | 1.8 |  |  |  | No of Seats | no of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-2 | BRITANNIA | yes | Subscribed | Metered | Rack | Caged | No of Racks | 11 | 11 | 0 | 11 | 0 |  | Rated | KVA | 60 | 87.52 | -27.52 | 0 | 0 | #REF! | 87.52 | 87.52 | 27.52 |  | Rated | 1.8 |  |  |  | No of Seats | no of seats | 0 | 0 | 0 | 0
L3 | DC-1 | VERSA NETWORKS INC | yes | Subscribed | Metered | Rack | Caged | No of Racks | 2 | 2 | 0 | 2 | 0 |  | Rated | KVA | 10 | 67.31 | -57.31 | 0 | 0 | #REF! | 67.31 | 67.31 | 57.31 |  | Rated | 1.8 |  |  |  | No of Seats | no of seats | 0 | 0 | 0 | 0
L3 | DC-3 | THE AHMEDNAGAR DISTRICT CENTRAL CO OP BANK LTD | [5 empty] | U Space | 21 | 21 | 0 | 21 | 0 |  | Rated | KVA | 1.5 | 0 | 1.5 | 0 | #REF! | #REF! | 0 | 0 | -1.5 |  | Rated | 1.8 |  |  |  | No of Seats | no of seats | 0 | 0 | 0 | 0
Note on J6: Vinoth Ramalingam: 18-08-2024 rack power on date
Note on R13: Vinoth Ramalingam: 4 Racks ( 7 to 10) in each 5Kva : total=20KVA 4Racks : 8KVA in each + Additional rated power 1kva : Total = 33KVA 2racks : 8KVA in each+ Additional rated power 14KVA : Total = 30KVA
Note on R20: Vinoth Ramalingam: 521005963: 1KVA additional power 27th MAR-24
Note on J22: Vinoth Ramalingam: 20-04-2024 rack power on
Note on J23: Vinoth Ramalingam: 2racks 800MM rack power on 3rd june 2025
Note on O25: 1 USD = Rs 65
Note on C26: 4 DID lines has been provided and billing paid by Admin.dotfinance Team
Note on S26: Informed to customer for regularize the power
Note on R27: 11 KVA (8+3) Rack downgrade (PO-18/19-20) 18/3/2020 521003914 - 2kva additional power . Total power 9Kva. 521004091 - PO-030/23-24( 2kva Add power) Total 11KVA 521006509: 1kva add power PO-032/24-25 Total Power: 12KVA
Note on S27: 8th Jan 2021 customer added 1 server,1 switch and 1 router. After adding new device power utilization will be : 8.63 KVA and additional power approval taken from customer
Note on K28: Vinoth Ramalingam: Jan 30 2022 customer new rack 600*1200 & 600*1800 rack provisioned in CSR8&9
Note on M28: 6+4+2+4 8th Jan 18U space allocated in BSR 4
Note on J29: 6+4+2+4 8th Jan 18U space allocated in BSR 4
Note on R29: 2.5 + addl 1.25 Kva+600Va for 1U +500Va +3kva
Note on S29: 6/9/2019 two dell server has been added in rack 7/11/19 4 Dell servers has been added 10/12/2019 Cisco switch has been added 08/01/2021 1/2 rack space with 3 KVA power provision done and customer added 2 server and 1 Switch. 9th july 23 installed dell server 800W
Note on M30: 3 racks with 1rack purchased on Jan 2022 so total rack is 4 Order Number:521002402 Rack Number: DSR3,DSR8 and DSR10. DSR10 rack Power On date 25th Aug 2022. DSR3 & DSR8 rack power on date:12th Sep 2022. Total 7 Racks 521004071 - 2rack with 12kva power. 521006028 - 1rack with 6kva power. ( DT:10-6-2024) 521006029 - 1rack with 6kva power. ( DT:10-6-2024) 521006636 - 1rack with 6KVA ( power on 1-10-2024) rack DSR 22
Note on R30: Bharath Kumar.k: Down graded from 2 rack to 1 rack and power also 12 KVA purchased
Note on J31: 3 racks with 1rack purchased on Jan 2022 so total rack is 4 Order Number:521002402 Rack Number: DSR3,DSR8 and DSR10. DSR10 rack Power On date 25th Aug 2022. DSR3 & DSR8 rack power on date:12th Sep 2022. Total 7 Racks 521004071 - 2rack with 12kva power. 521006028 - 1rack with 6kva power. ( DT:10-6-2024) 521006029 - 1rack with 6kva power. ( DT:10-6-2024) 521006636 - 1rack with 6KVA ( power on 1-10-2024) rack DSR 22
Note on R31: 2 Racks = 12KVA (each rack 6 KVA + 3.75 KVA +4 KVA Total = 19.75 KVA subscribed 1rack with 6 KVA power 2021 17th MAR 2021 additional 6KVA purchased Jan 2022 Customer Purchased 1 rack with 6KVA rated power. Aug 22 (ORD NO 521002402) customer purchased 3 racks with 18KVA Power. total power 521003722 - 6KVA additional power order purchased on 18-5-2022.Total 61.75KVA. 521004071 - July-23 2rack with 12kva power total power is 73.75KVA SO Rack Power 521004071 2 12 721000759 1 3 721006649 4 721000243 3.5 521002402 3 18 521003722 6 121001108 1 6 SO RACK Power 521001975 3 521003726 6 521003900 6 521001718 1 6 521000554 1 6 521006028 - 1rack with 6kva power. ( DT:10-6-2024) 521006576 - 6KVA add power 521006576: 6KVA Additional Power hence total power is 521006029 - 1rack with 6kva power. ( DT:10-6-2024) 521007315 : 6KVA additional power purchased 1st APR-25 total power 115.5KVA
Note on S31: New 1 Rack space provisioned and devices has been powered on(1.4 KVA rated power) 17th april 2020 Sep and Oct 2020 5 server has been added. ================ 4th nov 2020 3 server with 250 watts each. 10th nov 2020 2 server with 500 watts each has been installed 11th Dec 2020 customer removed 5 server having 250 watts power each Device power verification done on 18th Jan 2022 and observed all racks rated power is 29KVA and mail has been sent to customer. Apr-2022 new devices added in ESR 16, so power consumption is 39.58KVA. June 2022 ESR 16 customer added Tyron device so current power utilization is 40.35
Note on M33: Vinoth Ramalingam: Jan 2022 New rack purchased so total count 5(FSR9) 30-10-2023 fsr19 RACK POWER ON. Total 7racks.
Note on S33: Sep_2020 Old device has been removed and new devices has been added Jan 2022 customer removed and added few devices.
Note on J34: Vinoth Ramalingam: Jan 2022 New rack purchased so total count 5(FSR9) 30-10-2023 fsr19 RACK POWER ON. Total 7racks.
Note on R34: 9+2KVA additional Additional PO received 11.53 Total : 22.53 Additional 2KVA power PO received on 8th FEB 2021 8th FEB 2KVA additional power PO received 31-08-2021 2 KVA additional power purchased
Note on S34: Revised PO for power received on 24th Dec 2019 16/6/2020 one server has been added 9th sep 2020 customer removed 2 HP server and added 3 HP server having 500W capacity each 28th Nov HP server added(800W)
Note on J35: 13 U + 2U +2U+1U Sep 2022 2U space termination order received from Customer and sever also outwarded.
Note on R35: 3250 for 13 U + additional 2.87KVA + 500+500 + additional 190+750VA Dec1-2023 customer removed 2servers. Total power utilization is 3.01kva
Note on S35: partial services of 4U termination is in progress 04th Jan 2020 customer 2 server has been removed after that rated power will be : 4.93 KVA
Note on J36: Vinoth Ramalingam: 11th MAR 2025 new rack power on total rack count 2
Note on R36: Vinoth Ramalingam: PO Number & Date : IA/ITG/2021/10/22/01 – 20th Oct 2021 Additional 6KVA Rated power. 521005966: 3KVA Additional power. 521007092 : 1 Rack with 3KVA Power total power is 18KVA
Note on S36: Vinoth Ramalingam: June 2022 customer added new devices hence power consumption is 16.64KVA.
Note on J37: Additional 1U taken 521003388 - 2U total Uspace 8 3U Terminated, so total U space is 5U 521006875: 4U space
Note on M37: Vinoth Ramalingam: 21st FEB 2021 customer purchased new 1 rack , so 4+1=5 20th July customer disconnected 1 600*1000MM rack and power
Note on R37: 500+250VA additional power with 1U 521006875: 1KVA power
Note on J38: Vinoth Ramalingam: 21st FEB 2021 customer purchased new 1 rack , so 4+1=5 20th July customer disconnected 1 600*1000MM rack and power
Note on M38: Vinoth Ramalingam: 521005028 - ESR15 rack power date 12-3-2024 hence rack count 2
Note on R38: Additional power 4KVA per rack removed Additional 1 Rack with 8KVA power purchased on MAR 2nd 2021 As per PO:4200008680 Purchased power is 23KVA 521006730: Add 10KVA power purchased on 11th SEP 2024 total power 33KVA
Note on S38: A10 thunder 1040 2 devices has been added on July 30th and powered on Temporary purpose customer power on new HP encloser in new CTR 1 rack and device power consumption is 2650W 20th July 2021 customer disconnected 1 rack and powered off the devices. Sep 2022 customer installed new device hence power value is 18.40KVA.
Note on J39: Vinoth Ramalingam: 521005028 - ESR15 rack power date 12-3-2024 hence rack count 2 APR-25 customer disconnected 1 rack hence rack count is 1.
Note on M39: Vinoth Ramalingam: 10-5-2024 customer 1/2 rack power ON. Waiting for PO & SO.
Note on R39: Vinoth Ramalingam: 521005028 : 4KVA Power, hence total purchased power is 9KVA
Note on S39: Customer is installed new devices in ESAB rack on 13th March 2020(After adding power utilization is 7.23)
Note on J40: Vinoth Ramalingam: 10-5-2024 customer 1/2 rack power ON. Waiting for PO & SO.
Note on R40: Provision of 2 Dedicated Rack Space to accommodate standard 42-U rack with 600 mm width and 1200 mm depth. • Single phase rated power of 3 KVA per rack • Additional Rated power of 8 KVA, hence total allocation of 6KVA + 8KVA = 14 KVA for 2 Racks FEB 2022 Customer purchased 1/2 rack with 3.5KVA Power hence total power utilization is 17.5KVA 5th APRIL 2022 Customer purchased 8KVA Power 521003888 - Additional rated power 30KVA. total power is 37.5KVA
Note on S40: 21st oct 2020 new dell server has been added having 1600 watts of rated power. May-2022 New Dell Power store device added power capacity is 1450Watts Sep 2022 Customer installaed new device in DSR15 hence power consumption is 28.89KVA.
Note on S42: UPPCL additional power cabling has been done on 4th sep_2020 and ne HP device has been added on same day next month onwards power utilization will be 7.92 KVA Informed to customer to regularize the rated power
Note on S43: 15/12/2019 cisco device has been added
Note on S46: New device added on April
Note on M49: Vinoth Ramalingam: Sify/PBGB/2023/06 Dated 11.07.2023
Note on R52: Vinoth Ramalingam: 20th June 2021 8KVA power purchased along with 1 rack.( Order removed in system) Based on this PO:230401378(521002518) Half rack along with 4 KVA power has been proviosioned
Note on S52: Vinoth Ramalingam: Feb 8th 2022 customer power off the BSR 6 so power utilization is 4.64KVA
Note on C54: New DC hosted cloud customer So need to inform regularize the power
Note on S54: IBM devices rated power wrogly mentioned in old power inventory 3 IBM device power on 27th FEB 2021 device power : 2.98KV
Note on R55: additional power of 722 VA cost 28,855
Note on S56: Rack stack and power on has been done on 14th June 2020
Note on C57: 30th Dec 2020 devices has been powered on
Note on S57: Rack stack and power on has been done on 14th June 2020
Note on S58: Devices rack mounted and powered on 25th feb 2021
Note on J59: Vinoth Ramalingam: 20-08-2021 device power ON
Note on S59: Customer devices rack stack and powered on 20-08-2021
Note on J60: Vinoth Ramalingam: 20-08-2021 device power ON
Note on S60: Customer devices rack stack and powered on 28-08-2021
Note on M61: Vinoth Ramalingam: 20-08-2021 device power ON
Note on S61: Devices rack mounted and powered on 12th Jan 2020 Microscan 2 devices power off on Aug 2021
Note on J62: Vinoth Ramalingam: 31st Aug 2021 2 U + 500VA Purchased. Jan 2023 1 U + 250VA purchased.
Note on R62: Vinoth Ramalingam: Order Number Space Power 521001029 2 U 500VA 521003275 1U 250VA 521003878 250VA 1000VA
Note on S62: 18th feb 2022 rack power on. Apr-23 new HP 360 Gen 10 server power on hence 1.38Kva
Note on J63: Vinoth Ramalingam: 11th APRIL 2022 rack powered on.
Note on R63: Vinoth Ramalingam: Order Number Space Power 521001029 2 U 500VA 521003275 1U 250VA 521003878 250VA 1000VA
Note on S63: Customer devices rack stack and powered on 20-08-2021
Note on J64: Vinoth Ramalingam: Rack Power on date is 08-07-2022
Note on M64: Vinoth Ramalingam: 31st Aug 2021 2 U + 500VA Purchased. Jan 2023 1 U + 250VA purchased.
Note on S64: New device added on April
Note on J65: Vinoth Ramalingam: power on 05-07-2022
Note on M65: Vinoth Ramalingam: 11th APRIL 2022 rack powered on.
Note on S65: New device added on April
Note on J66: Vinoth Ramalingam: power on 05-07-2022
Note on M66: Vinoth Ramalingam: Rack Power on date is 08-07-2022
Note on S66: New device added on April
Note on J67: Vinoth Ramalingam: 521003975 - 1st FEB-23 2 rack along with 12 kva power proviosioned.
Note on M67: Vinoth Ramalingam: power on 05-07-2022
Note on J68: Vinoth Ramalingam: 521003975 - 1st FEB-23 2 rack along with 12 kva power proviosioned.
Note on M69: Vinoth Ramalingam: 521003975 - 1st FEB-23 2 rack along with 12 kva power proviosioned.
Note on J70: Vinoth Ramalingam: 521004927 - 21U with 1.75KVA Rated power has been proviosioned on 8th MAR-24
Note on R70: Vinoth Ramalingam: 521004927 - 21U with 1.75KVA Rated power has been proviosioned on 8th MAR-24
Note on J71: Vinoth Ramalingam: 521005019 - 4U space along with 1KVA Power has been proviosioned on 8th MAR-24
Note on R71: Vinoth Ramalingam: 521005019 - 4U space along with 1KVA Power has been proviosioned on 8th MAR-24
Note on S71: New device added on April
Note on J72: Vinoth Ramalingam: 22-08-2024 power on date
Note on M72: Vinoth Ramalingam: 521005019 - 4U space along with 1KVA Power has been proviosioned on 8th MAR-24
Note on J73: Vinoth Ramalingam: 28-10-2024 power on date
Note on M73: Vinoth Ramalingam: 521005062 - 4U with 1 KVA power proviosioned on 6th MAR-24
Note on J74: Vinoth Ramalingam: 28-10-2024 power on date
Note on M74: Vinoth Ramalingam: 18-8-2024 power on date
Note on C75: 5+11+30 Racks
Note on M75: Vinoth Ramalingam: 18-8-2024 power on date
Note on R75: 36+84
Note on C76: 5+11+30 Racks
Note on R76: 36+84
Note on C77: changed from rated to subcribe since mesurement of power usage avilable in meter and 5 KVA kept for future use
Note on S77: New RTS devices are added in noc room and each RTR which can hold 600 W power
Note on J79: Vinoth Ramalingam: 20th June-25 customer rack power on.
Note on J80: Vinoth Ramalingam: 27th June-25 rack power on
Note on AF80: Add-on 3 Racks one Power ON 9th FEB-26
Note on S87: New RTS devices are added in noc room and each RTR which can hold 600 W power
Note on J88: Vinoth Ramalingam: 25th NOV 2025 power on
Note on M88: Vinoth Ramalingam: 18-8-2024 power on date

## Disconnection details
[19 empty] | Divisification |  | 0.5 | Rated to Consumed |  |  | #REF! |  | Actual PUE | #REF! | Actual Unit Rate: | #REF! | #REF! | Genset Hr/Mo | 5
|  |  |  | Billing Model |  | Space | [8 empty] | Power Capacity | [11 empty] | Power Usage |  |  |  |  | Seating Space | [7 empty] | Revenue (Monthly ) | [6 empty] | Contract Information
Floor | Floor / Module | Customer Name | RHS/SH | Power Subscription Model (Rated/Subscribed) | Power Usage Model (Bundled / Metered) | Subscription Mode | Caged /Uncaged | UoM | Subscription | In Use | Yet to be given/ | Billed | Reserved Capacity if any (Non-Billable) | Per Unit rate (MRC) | Subscription Model | UoM | Total Capacity Purchased | Capacity in Use | Capacity to be given | Reserved Capacity if any | Subscribed Capacity to be given in KW | "Allocated" Capacity in KW | DC NW Infra | Usage in KW | Billable Additional Capacity | Additional Capacity Charges (MRC) | Usage Model | Multiplier | Unit rate Model (Fixed/Variable) | Unit Rate (per KW-HR) | No Of Units (KW-HR/ Month | Subscription Model | UoM | Subscription | In Use | Yet to be given | Billed | Reserved Capacity if any | Per Unit rate | Space revenue including capacity | Additional Capacity Revenue | Power Usage revenue | Seating Space | Any Other Items | Total Revenue | Billing Frequency | Sales Order ref No | Contract Start Date | Term of Contract (No of Years) | Current Expiry Date | Remarks if any | Cross connect
L3 | DC-2 | BESCOM | yes | Rated | Bundled | Rack | Caged | No of Racks | 33 | 33 | 0 | 33 | 0
L3 | DC-2 | Timesofmoney(Unimoni Enterprise Solutions Pvt. Ltd) | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0
L3 | DC-1 | TechM WAAS(ING) | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0
L3 | DC-3 | Shapoorji Pallonji | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 3 | 3 | 0 | 3 | 0
L3 | DC-1 | FedBank | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0
L3 | DC-2 | Sungard | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 | 0
L3 | DC-1 | Star union daichi | yes | Subscribed | Metered | Rack | Caged | No of Racks | 5 | 5 | 0 | 5 | 0
L3 | DC-3 | India Post payment bank Ltd | No | Subscribed | Metered | Rack | Caged | No of Racks | 19 | 19 | 0 | 19 | 0 | 27646.1974 | Subscribed | KVA | 58 | 27.35 | 30.65 | 0 | 30.65 | 58 | 27.35 | 27.35 | -30.65 |  | Metered | 1 | Fixed | 15 | 37695.3 | No of Seats | No of seats | 6 | 6 | 0 | 6 | 0 | 8333.3333 | 525277.75 |  | 565429.5 | 50000 |  | 1140707.25 | [7 empty] | Disconnected on 15 March 2025
L3 | DC-1 | BAJAJ FINANCIAL SECURITIES LTD | Yes | Rated | Bundled | U space | Uncaged | U Space | 2 | 5 | -3 | 4 | -2 | 4140.625 | Rated | KVA | 0.5 | 0.186 | 0.314 | 0 | #VALUE! | #VALUE! | 0.186 | 0.186 | -0.314 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | UCO BANK 2 - Temp | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 4 | 4 | 0 | 4 | 0 |  | Rated | KVA | 29 | 28.96 | 0.04 | 0 | #VALUE! | #VALUE! | 28.96 | 28.96 | -0.04 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0
L3 | DC-1 | kfintek | yes | Subscribed | Metered | Rack | Uncaged | No of Racks | 10 | 10 | 0 | 10 | 0 |  | Subscribed | KW | 30 | 17.35 | 12.65 | 0 | 12.65 | 30 | 17.35 | 17.35 | -12.65 |  | Metered | 1.8 |  |  | 0 | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0
L3 | DC-1 | TECHNO TRUST SOLUTIONS | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 2500 | Rated | KVA | 4 | 6.2 | -2.2 | 0 | 0 | 2 | 6.2 | 6.2 | 2.2 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 1 | 1 | 0 | 1 | 0 |  | 2500 |  | 0 | 0 |  | 2500
L3 | DC-1 | ASB International | Yes | Rated | Bundled | U space | Uncaged | U Space | 4 | 4 | 0 | 4 | 0 | 1428.5714 | Rated | KVA | 1 | 0.847 | 0.153 | 0 | #REF! | #REF! | 0.847 | 0.847 | -0.153 | 7500 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 5714.2857 |  | 0 | 0 |  | 5714.2857
L3 | DC-1 | Que Processing Service Ltd | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 2.77 | 0.06 | 2.71 | 0 | #REF! | #REF! | 0.06 | 0.06 | -2.71 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | SH Kelkar | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 | 3110.6618 | Rated | KVA | 3 | 2.25 | 0.75 | 0 | #REF! | #REF! | 2.25 | 2.25 | -0.75 | 7916.6667 | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0 |  | 3110.6618 |  | 0 | 0 |  | 3110.6618
L3 | DC-1 | AKSHAYAPATRA FOUNDATION | Yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 3 | 4.06 | -1.06 | 0 | 0 | #REF! | 4.06 | 4.06 | 1.06 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | DEEPIJA TELECOM PRIVATE LIMITED | yes | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 | 0 |  | Rated | KVA | 3 | 2.99 | 0.01 | 0 | #REF! | #REF! | 2.99 | 2.99 | -0.01 | 8166.6667 | Rated | 1.8 |  |  |  | No of Seats | no of seats | 0 | 0 | 0 | 0 | 0
L3 | DC-1 | CITO INFOTECH PRIVATE LIMITED | yes | Rated | Bundled | U space | Uncaged | U Space | 3 | 3 | 0 | 3 | 0 |  | Rated | KVA | 0.6 | 0.893 | -0.293 | 0 | 0 | #REF! | 0.893 | 0.893 | 0.293 |  | Rated | 1.8 |  |  |  | No of Seats | No of seats | 0 | 0 | 0 | 0 | 0
Note on C4: Vinoth Ramalingam: 19th APR 2024 power off
Note on C5: Vinoth Ramalingam: 5th June -24 disconnected
Note on C6: Vinoth Ramalingam: 17-5-2024 disconnect
Note on C7: Vinoth Ramalingam: 9th july 2024 disconnected
Note on C8: Vinoth Ramalingam: 27-7-2024 power off
Note on C9: Vinoth Ramalingam: 31st July 2024 Power off
Note on C10: Vinoth Ramalingam: 24-09-2024 disconnection
Note on C11: Vinoth Ramalingam: Disconnection date 13th FEB 2025
Note on C13: Vinoth Ramalingam: 2nd may-25 power off
Note on J13: Vinoth Ramalingam: Sify/PBGB/2023/06 Dated 11.07.2023
Note on M13: Vinoth Ramalingam: Sify/PBGB/2023/06 Dated 11.07.2023
Note on R13: Vinoth Ramalingam: Sify/PBGB/2023/06 Dated 11.07.2023 - 4rack 6KVA Rated + 7KVA Additional power
Note on C14: 26th June Power Off
Note on C15: Vinoth Ramalingam: 4th SEP-2025 power off
Note on M15: Additional 1U taken 521003388 - 2U total Uspace 8 3U Terminated, so total U space is 5U 521006875: 4U space
Note on S15: Vinoth Ramalingam: MAR-23 customer removed technotrust devices and mounted in GSR rack.
Note on S17: Devices rack mounted and powered on 12th Jan 2020 Microscan 2 devices power off on Aug 2021
Note on C18: Vinoth Ramalingam: 30th DEC 2025 disconnected the services
Note on M18: 13 U + 2U +2U+1U Sep 2022 2U space termination order received from Customer and sever also outwarded.
Note on C19: 30th Dec 2020 devices has been powered on
Note on S19: Devices rack mounted and powered on 25th feb 2021
Note on C20: Vinoth Ramalingam: 3rd NOV 2025 power off
Note on J20: Vinoth Ramalingam: 521005019 - 4U space along with 1KVA Power has been proviosioned on 8th MAR-24
Note on M20: Vinoth Ramalingam: 521004927 - 21U with 1.75KVA Rated power has been proviosioned on 8th MAR-24
Note on R20: Vinoth Ramalingam: 521005019 - 4U space along with 1KVA Power has been proviosioned on 8th MAR-24
Note on S20: New device added on April
Note on C21: 21st FEB 2026 power off
Note on S21: New RTS devices are added in noc room and each RTR which can hold 600 W power