## Summary
Description | Value | Actual Load KVA
| As per the Sanction Letter | Usage measured on 1of every month
Utility Sanction Load KVA | 14000 KVA | 7760 KVA
Utility Minimum Demand % | 75
Capacity Installed | Transformer kW | No of TX | Catcher TX kW | No. Of catcher | Actual Load kW | Generator kW | No of DG | Catcher DG kW | No. Of catcher | UPS kW | UPS Config | IT capacity Installed kW | IT Power Sold in kW ( concidering unity as PF) | Allocated IT Power to customer ( Taking 50% as divercity factor for rated power customer ) | IT kW Usage | Avaialble IT kW Design-Used | Available IT kW Design-Sold | Available IT kW Design-Sold ( Allocated capacity) | MAX Rack Capacity | Racks which can be placed on floor | Rack losss ( Cage+ non standard rack+ path) | Available space | Designed White Space ( in SQ FT) | Used White Space( in SQ FT) | Avaialble White Space ( in SQ FT)
| Mention the design kW capacity of Transformer |  |  |  |  | Mention the design kW capacity of Generator |  |  |  | Mention the design N capacity in kw in a N+N Configuration |  | Installed including interfloor shared capacity | Customer subscribed IT kW | Allocated power | Measured on 1st of every month | Measured on 1st of every month | Measured on 1st of every month | Measured on 1st of every month
L1 | 2475 | 1 | 2475 | 1 | 1046 | 2400 | 1 | 2400 | 1 | 2160 | Bank A ( 1250 KVA* 2) & Bank B (600 KVA *4 ) | 2160 | 2160 | 2160 | #REF! | #REF! | 0 | 0 | 220 | 220 | 0 | 0 | 7384 | 7384 | 0
L2 | 2475 | 1 |  |  | 860 | 2400 | 1 |  |  | 2160 | Bank A ( 1250 KVA* 2) & Bank B (600 KVA *4 ) | 2160 | 2160 | 2160 | #REF! | #REF! | 0 | 0 | 220 | 220 | 0 | 0 | 7384 | 7384 | 0
L3 | 2475 | 1 |  |  | 837 | 2400 | 1 |  |  | 2160 | Bank A ( 1250 KVA* 2) & Bank B (600 KVA *4 ) | 2160 | 2160 | 2160 | #REF! | #REF! | 0 | 0 | 220 | 220 | 0 | 0 | 7384 | 7384 | 0
L4 | 2025 | 1 | 2250 | 1 | 1048 | 1600 | 1 | 2000 | 1 | 1440 | Bank A ( 400 KVA* 4) & Bank B (400 KVA *4 ) | 1440 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 392 | #REF! | 69 | #REF! | 7300 | 7300 | 0
L5 | 2025 | 1 |  |  | 1062 | 1800 | 1 |  |  | 1440 | Bank A ( 400 KVA* 4) & Bank B (400 KVA *4 ) | 820 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 353 | #REF! | 50 | #REF! | 9200 | 9200 | 0
L6 | [11 empty] | 620 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 258 | #REF! | 34 | #REF! | 6000 | 6000 | 0
L7 | 2250 | 1 |  |  | 193 | 1800 | 1 |  |  | 1700 | Bank A ( 450 KVA* 4) & Bank B (450 KVA *4 ) | 1400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 261 | #REF! | 13 | #REF! | 6850 | 6850 | 0 | From L7 To L6 & l5 =150 KVA L6+ 120 KVA L5
Total | [9 empty] | 11060 |  | 10760 | #REF! | #REF! | #REF! | #REF! |  |  | 1924 | #REF! | 166
[19 empty] | 1924 | #REF!

## Terminated
[18 empty] | Divisification |  | 0.5 | Rated to Consumed |  | #REF! |  | Actual PUE | 2.21 | Actual Unit Rate: | 10.35 | 18246.9202 | Genset Hr/Mo | 70.5
|  |  | Billing Model |  | Space | [8 empty] | Power Capacity | [10 empty] | Power Usage |  |  |  |  | Seating Space | [7 empty] | Revenue (Monthly ) | [6 empty] | Contract Information
Floor | Floor / Module | Customer Name | Power Subscription Model (Rated/Subscribed) | Power Usage Model (Bundled / Metered) | Subscription Mode | Caged /Uncaged | UoM | Subscription | In Use | Yet to be given/ | Billed | Reserved Capacity if any (Non-Billable) | Per Unit rate (MRC) | Subscription Model | UoM | Total Capacity Purchased | Capacity in Use | Capacity to be given | Reserved Capacity if any | Subscribed Capacity to be given in KW | "Allocated" Capacity in KW (for KVA subscribed customer 50% diversity is used to make kW ) | DC NW Infra | Billable Additional Capacity | Additional Capacity Charges (MRC) | Usage Model | Multiplier | Uit rate Model (Fixed/Variable) | Unit Rate (per KW-HR) | No Of Units (KW-HR/ Month | Subscription Model | UoM | Subscription | In Use | Yet to be given | Billed | Reserved Capacity if any | Per Unit rate | Space revenue including capacity | Additional Capacity Revenue | Power Usage revenue | Seating Space | Any Other Items | Total Revenue | Billing Frequency | Sales Order ref No | Contract Start Date | Term of Contract (No of Years) | Current Exiry Date | Remarks if any | Avg revenue /Rack /Month | Avg revenue /KW /Month | Net Revenue / Resvd KW | Proj Net Revenue / Resvd KW | Sold Net Revenue / Resvd KW | Total Rev (Cap + Power) | Capacity Revenue | Power Revenue | Cost of Power @ Act Usage | Proj Cost of Power @ Reserv Cap | Cost of Power @ Design Use | Net Rev Total | Target Capacity Revenue | Capacity Surplus/Leakage | Power Surplus/Leakage | Contribution to Target | KW |  | Power Surplus/Leakage | Capacity Surplus/Leakage | Total Surplus/Leakage | Power Surplus/Leakage / KW | Capacity Surplus/Leakage / KW | Total Surplus/Leakage / KW
L5 | L5A-05-11 | KESCO (Kanpur Elec) | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 0 | 1 | 0 |  | 51666.6667 | Rated | KVA | 0 | 0 | 0 |  | 0 | #REF! | 0 | 0 | 0 | Bundled | [8 empty] | 0 |  |  |  | 0 | 0 | 0 | 0 | 26719.9722 | 26719.9722 |  | 721003675 & 711080579 |  |  |  |  | 26719.9722 | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L4 | L4-F-24 & L4-F-29 | Adani Wilmar Limited | Rated | Bundled | Rack | Uncaged | No of Racks | 4 | 0 | 0 | 0 |  | 42333.3333 | Rated | KVA | 0 | 0 | 0 |  | 0 | #REF! | 0 | 0 | 5833.3333 | Bundled | [8 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 22750 | 22750 |  | 121000894 & 121000913 | 2020-01-01 | 1 | 2020-12-31 |  | 5687.5 | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5B-01-05 & L5B-01-06 | MJUNCTION SERVICES LIMITED | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 0 | 0 | 0 |  | 66666.6667 | Rated | KVA | 0 | 0 | 0 |  | 0 | #REF! | 0 | 0 | 6666.6667 | Bundled |  |  |  |  | No of Seats | No of Seats | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 721004949 |  |  |  |  | 0 | #REF! | #REF! | #REF! | #REF! | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L4 | L4-E-29 | E2 Info Solution | Rated | Bundled | U space | Uncaged | U Space | 2 | 0 | 2 | 0 |  | 2291.6667 | Rated | KVA | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 7500 | Bundled | [8 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #REF! | #REF! | 0 | 0 | 0 | #DIV/0! | #REF! | #REF! | #REF! | #REF! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
L6 | L6-F-25 | NGC Broadband | Rated | Bundled | U space | Uncaged | U Space | 2 | 2 | 0 | 2 |  | 2916.6667 | Rated | KVA | 0.5 | 0.28 | 0.22 |  | 0.11 | 0.25 |  | 0 | 8250 | Bundled | [8 empty] | 0 |  |  |  | 5833.3333 | 0 | 0 | 0 | 0 | 5833.3333 | [6 empty] | 116666.6667 | 23333.3333 | 23333.3333 | 15304.6884 | 5086.4131 | 5833.3333 | #REF! | #REF! | 0 | 2007.1612 | 4561.7301 | 5833.3333 | #REF! | #REF! | #REF! | #REF! | 0.25 | 23333.3333 | 4561.7301 | #REF! | #REF! | 18246.9202 | #REF! | #REF!
L6 | L6-D-30, L6-D-29 | ECSO | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 0 | 2 | 0 |  | 48333.3333 | Rated | KVA | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9166.6667 | Bundled | [8 empty] | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #REF! | #REF! | 0 | 0 | 0 | #DIV/0! | #REF! | #REF! | #REF! | #REF! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
L5 | Server Hall 5A L5A-01-08 | RACSANN TECHNOLOGIES PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 5 | 5 | 0 | 5 |  | 2500 | Rated | KVA | 1.25 | 1.01 | 0.24 |  | #VALUE! | #VALUE! |  | 0 | 8750 | Bundled | [8 empty] | 0 |  |  |  | 12500 | 0 | 0 | 0 | 7500 | 20000 |  | 121001215 |  |  |  |  | 160000 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 12500 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L4 | Server Hall L4 L4-D-29 | Balaji Teleworks | Rated | Bundled | U space | Uncaged | U Space | 6 | 6 | 0 | 6 |  | 3194.4444 | Rated | KVA | 0.55556 | 1.11 | -0.55444 |  | 0 | #VALUE! |  | 0.55444 | 8250 | Bundled | [8 empty] | 0 |  |  | 0 | 19166.6667 | 4574.1667 | 0 | 0 | 0 | 23740.8333 | [6 empty] | 158272.2222 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 23740.8333 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L6 | Server Hall L6 L6-E-03 | SAIKRITI TECHSOFT PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 21 | 21 | 0 | 21 |  | 1388.8889 | Rated | KVA | 1.5 | 3.38 | -1.88 |  | 0 | #VALUE! |  | 1.88 | 8333.3333 | Bundled | [8 empty] | 0 |  |  |  | 29166.6667 | 15666.6667 | 0 | 0 | 0 | 44833.3333 | [6 empty] | 85396.8254 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 44833.3333 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L6 | Server Hall L6 L6-F-25 | ACME DIGINET CORPORATION PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 6 | 6 | 0 | 6 |  | 2416.6667 | Rated | KVA | 1.5 | 2.67 | -1.17 |  | 0 | #VALUE! |  | 1.17 |  | Bundled | [8 empty] | 0 |  |  |  | 14500 | 0 | 0 | 0 | 0 | 14500 | [6 empty] | 96666.6667 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 14500 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L4 | Server Hall L4 L4-D-29 | NAS INTERNET SERVICES PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 3 | 3 | 0 | 3 |  | 2916.6667 | Rated | KVA | 0.75 | 0.61 | 0.14 |  | #VALUE! | #VALUE! |  | 0 | 7500 | Bundled | [8 empty] | 0 |  |  | 0 | 8750 | 0 | 0 | 0 | 0 | 8750 | [6 empty] | 116666.6667 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 8750 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L5 | Server Hall 5A L5A-04-11 | SIMPLE TELECOM PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 11 | 11 | 0 | 11 |  | 909.0909 | Rated | KVA | 1 | 2.1 | -1.1 |  | 0 | #VALUE! |  | 1.1 |  | Bundled | [34 empty] | #VALUE! | [5 empty] | #VALUE!
L7 | L7-E-05 | SWAKSH INFRATECH | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 37500 | Rated | KVA | 3 | 0 | 3 |  | #REF! | #REF! | 0 | 0 |  | Bundled | [8 empty] | 0 |  |  | 0 | 37500 | 0 | 0 | 0 | 0 | 37500 | [6 empty] | 37500 | #REF! | #REF! | #REF! | #REF! | 37500 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5A-02-02, L5A-02-03, L5A-02-04, L5A-02-05, L5A-02-06 & L5A-02-10 | L&T (RVNL) | Rated | Bundled | Rack | Uncaged | No of Racks | 6 | 6 | 0 | 6 |  | 59361.2778 | Rated | KVA | 84.65 | 84.65 | 0 |  | 0 | #REF! | 14.66 | 0 | 7725 | Bundled | [8 empty] | 0 |  |  |  | 356167.6667 | 0 | 0 | 0 |  | 356167.6667 |  | Renewal | 2020-04-01 | 1 | 2021-03-31 |  | 59361.2778 | #REF! | #REF! | #REF! | #REF! | 356167.6667 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L6 | L6-B-33 | DEHRADUN E NET SOLUTIONS (P) LTD. | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 36875 | Rated | KVA | 3.5 | 3.33 | 0.17 |  | #REF! | #REF! | 2.41 | 0 | 7500 | Bundled | [8 empty] | 0 |  |  |  | 36875 | 0 | 0 | 0 |  | 36875 | [6 empty] | 36875 | #REF! | #REF! | #REF! | #REF! | 36875 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L6 | L6-D-03 | EMINENCE SOFTECH PVT LTD | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 22500 | Subscribed | KW | 3 | 0.037634 | 2.9624 |  | 2.9624 | 3 | 0.037634 | 0 | 7916.6667 | Metered | 1 | Fixed | 17 | 28 |  |  |  |  | 0 |  |  | 0 | 22500 | 0 | 476 | 0 | 0 | 22976 | [6 empty] | 22976 | 7658.6667 | #REF! | #REF! | #REF! | 22976 | 22500 | 476 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L7 | L7-F-26 to L7-F-29 | NEXTRA ONLINE SERVICES PRIVATE LIMITED | Subscribed | Metered | Rack | Uncaged | No of Racks | 4 | 4 | 0 | 4 |  | 31100 | Subscribed | KW | 16.6 | 6.8954 | 9.7046 |  | 9.7046 | 16.6 | 6.8954 | 0 | 0 | Metered | 1 | Fixed | 0 | 4964.7 |  |  |  |  | 0 |  |  | 0 | 124400 | 0 | 0 | 0 | 0 | 124400 | [6 empty] | 31100 | 7493.9759 | #REF! | #REF! | #REF! | 124400 | 124400 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 16.6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | Server Hall 5A L5A-04-11 | NESECURE TELECOM | Rated | Bundled | U space | Uncaged | U Space | 6 | 6 | 0 | 6 |  | 1666.6667 | Rated | KVA | 1 | 0.05 | 0.95 |  | 9.2194 | 9.7046 |  | 0 | 9166.6667 | Bundled | [8 empty] | 0 |  |  |  | 10000 | 0 | 0 | 0 | 0 | 10000 | [6 empty] | 66666.6667 | 1030.4409 | #VALUE! | #VALUE! | #VALUE! | 10000 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 9.7046 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L4 | L4-E-27 & L4-E-28 | CLOUDFLARE INC | Subscribed | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 |  | 1840 | Subscribed | KVA | 14.36 | 8.0506 | 6.3094 |  | 6.3094 | 14.36 | 7.2456 | 0 | 250 | Bundled | 1 | Fixed | 0 | 5216.81 |  |  |  |  | 0 |  |  |  | 3680 | 0 | 0 | 0 | 0 | 3680 |  | 121000084 |  |  |  |  | 1840 | 256.2674 | #VALUE! | #VALUE! | #VALUE! | 3680 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | 14.36 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L6 | L6-D-01, L6-D-02 | Cloudflare | Subscribed | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 |  | 1840 | Subscribed | KW | 13 | 0 | 13 |  | 13 | 13 | 0 | 0 | 283 | Bundled | 1 | Fixed | 0 | 0 |  |  |  |  | 0 |  |  |  | 3680 | 0 | 0 | 0 | 0 | 3680 | [6 empty] | 1840 | 283.0769 | #VALUE! | #VALUE! | #VALUE! | 3680 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L4 | L4-F-30 | CP WHOLESALE INDIA PVT LTD | Rated | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 30000 | Rated | KVA | 9 | 9 | 0 |  | 0 | #VALUE! | 0.81202 | 0 | 0 | Metered | 1 | Fixed | 17 | 604.14 |  |  |  |  | 0 |  |  |  | 30000 | 0 | 10270.38 | 0 | 50000 | 90270.38 |  | 721005527 & 711120937 |  |  |  |  | 90270.38 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 40270.38 | 30000 | 10270.38 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #REF! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L4 | L4-E-33 | CP WHOLESALE INDIA PVT LTD | Rated | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 35972.2222 | Rated | KVA | 8 | 10.62 | -2.62 |  | 0 | #VALUE! | 4.4698 | 2.62 | 7500 | Metered | 1 | Fixed | 15.75 | 3325.52 |  |  |  |  | 0 |  |  |  | 35972.2222 | 19650 | 52376.94 | 0 | 50000 | 157999.1622 |  | 721005527 & 711120937 |  |  |  |  | 157999.1622 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 107999.1622 | 55622.2222 | 52376.94 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #REF! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L7 | L7-A-15, L7-A-16, L7-A-17 & L7-A-18 | Stackpath | Subscribed | Metered | Rack | Caged | No of Racks | 4 | 4 | 0 | 4 |  | 0 | Subscribed | KW | 30 | 12.1669 | 17.8331 |  | 17.8331 | 30 | 12.1669 | 0 | 0 | Metered |  | Fixed | 0 | 9052.2 |  |  |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | #REF! | #REF! | #REF! | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 30 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L4 | L4-E-23 | iBOSS, INC. | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 75833.3333 | Rated | KVA | 5 | 19.62 | -14.62 |  | 0 | #REF! | 5.49 | 14.62 | 0 | Bundled | [8 empty] | 0 |  |  | 0 | 75833.3333 | 0 | 0 | 0 | 131541.6667 | 207375 |  | 121000513 | 2019-08-23 | 3 | 2022-08-22 |  | 207375 | #REF! | #REF! | #REF! | #REF! | 75833.3333 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L7 | L7-F-25 | ONEOTT INTERTAINMENT LTD | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  |  | Subscribed | KW | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 0 | 0 |  | Metered
L5 | L5A-01-06 | STAR BROADBAND SERVICES I PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 |  | 4583.3333 | Rated | KVA | 0.25 | 0.26 | -0.01 |  | 0 | #VALUE! |  | 0.01 | 7500 | Bundled | [8 empty] | 0 |  |  |  | 4583.3333 | 75 | 0 | 0 | 12500 | 17158.3333 |  | 121000867 |  |  |  |  | 686333.3333 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4658.3333 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L5 | L5A-02-01 | PRACTION NETWORKS PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 4 | 4 | 0 | 4 |  | 2916.6667 | Rated | KVA | 1 | 0.17 | 0.83 |  | #VALUE! | #VALUE! |  | 0 | 9166.6667 | Bundled | [8 empty] | 0 |  |  |  | 11666.6667 | 0 | 0 | 0 | 13333.3333 | 25000 |  | 121000185 |  |  |  |  | 250000 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 11666.6667 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
L4 | Server Hall L4 L4-D-29 | SPEEDNET UNIQUE NETWORK PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 1 | 1 | 0 | 1 |  | 2916.6667 | Rated | KVA | 0.25 | 0.13 | 0.12 |  | 0 | 0 |  | 0 | 0 | Bundled | [8 empty] | 0 |  |  | 0 | 2916.6667 | 0 | 0 | 0 | 0 | 2916.6667 | [6 empty] | 116666.6667 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2916.6667 | #REF! | #REF! | 0 | 0 | 0 | #DIV/0! | #REF! | #REF! | #REF! | #REF! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
L4 | Server Hall L4 L4-E-29 | FIBLIB DIGITAL NETWORKS | Rated | Bundled | U space | Uncaged | U Space | 2 | 2 | 0 | 2 |  | 3125 | Rated | KVA | 0.5 | 0.25 | 0.25 |  | 0 | 0 |  | 0 |  | Bundled | [8 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #REF! | #REF! | 0 | 0 | 0 | #DIV/0! | #REF! | #REF! | #REF! | #REF! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
L6 | L6-G-26 to L6-G-33, L6-F-26 to L6-F-33 | GLORYBIRD INDIA PRIVATE LIMITED | Subscribed | Bundled | Rack | Uncaged | No of Racks | 16 | 16 | 0 | 16 |  | 127680 | Subscribed | KW | 78 | 0 | 78 |  | 78 | 78 | 0 | 0 | 0 | Bundled | 1 | Fixed | 0 | 0 |  |  |  |  | 0 |  |  | 0 | 2042880 | 0 | 0 | 0 | 0 | 2042880 | [6 empty] | 127680 | 26190.7692 | #REF! | #REF! | #REF! | 2042880 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 78 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L6 | Server Hall L6 L6-F-24 | IPNET BROADBAND NETWORK PVT LTD ( 29U TO 30U) | Rated | Bundled | U space | Uncaged | U Space | 2 | 2 | 0 | 2 |  | 1500 | Rated | KVA | 0.3 | 0.04 | 0.26 |  | 0 | 0 |  | 0 |  | Bundled | [8 empty] | 0 |  |  |  | 3000 | 0 | 0 | 0 | 0 | 3000 | [6 empty] | 60000 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3000 | #REF! | #REF! | 0 | 0 | 0 | #DIV/0! | #REF! | #REF! | #REF! | #REF! | 0 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
L4 | L4-C-28 | UNITAS GLOBAL INDIA PVT LTD | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 56816.6667 | Rated | KVA | 5 | 3.56 | 1.44 |  | 0 | 0 | 0.91 | 0 | 10000 | Bundled | [8 empty] | 0 |  |  | 0 | 56816.6667 | 0 | 0 | 0 | 100380 | 157196.6667 |  | 121001564 |  |  |  |  | 157196.6667 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 56816.6667 | #REF! | #REF! | 64.155 | 64.155 | 0 | #DIV/0! | #REF! | #REF! | #REF! | #REF! | 0 | #DIV/0! | -64.155 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | #DIV/0!
L4 | L4-C-29 | SUBSPACE COMMUNICATION LLC | Subscribed | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 75600 | Subscribed | KW | 4 | 0.35442 | 3.6456 |  | 3.6456 | 4 | 0.35442 | 0 | 0 | Bundled |  |  |  | 255.18 |  |  |  |  | 0 |  |  | 0 | 75600 | 0 | 0 | 0 | 0 | 75600 | [6 empty] | 75600 | 18900 | #DIV/0! | #DIV/0! | #DIV/0! | 75600 | #REF! | #REF! | 24.9864 | 282 | 282 | #DIV/0! | #REF! | #REF! | #REF! | #REF! | 4 | #DIV/0! | 257.0136 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | #DIV/0!
L5 | L5A-01-01 | THE NAGALAND STATE CO-OPERATIVE BANK LTD | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 6666.6667 | Rated | KVA | 3 | 4.49 | -1.49 |  | 0 | #REF! | 1.17 | 1.49 | 0 | Bundled | [8 empty] | 0 |  |  |  | 6666.6667 | 0 | 0 | 0 | 833.3333 | 7500 |  | Renewal |  |  |  |  | 7500 | #REF! | #REF! | #REF! | #REF! | 6666.6667 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5A-01-11 | PEERCAST TELECOM INDIA PRIVATE LIMITED | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 15666.6667 | Subscribed | KW | 3 | 1.5194 | 1.4806 |  | 1.4806 | 3 | 1.5194 | 0 |  | Metered | 1 | Fixed |  | 1130.46 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | [6 empty] | 0 | 0 | #VALUE! |  |  | 0 | 0 | 0 | #VALUE! |  |  | #VALUE! | #REF! | #REF! | #VALUE! | #REF! | 3 | #VALUE! | #VALUE! | #REF! | #VALUE! | #VALUE! | #REF! | #VALUE!
L5 | L5A-02-01 | ISHAN NETSOL PVT LTD | Rated | Bundled | U space | Uncaged | U Space | 5 | 5 | 0 | 5 |  | 2083.335 | Rated | KVA | 1.25 | 0.78 | 0.47 |  | 0 | 0 | 0.66 | 0 | 7500 | Bundled | [8 empty] | 0 |  |  |  | 10416.675 | 0 | 0 | 0 | 9334 | 19750.675 |  | 121000328 |  |  |  |  | 158005.4 | #DIV/0! | 3.878 | 3.878 | 1.2445 | 10416.675 | #REF! | #REF! | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | 0 | 3.878 | 0 | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5A-07-05, L5A-07-06, L5A-07-07, L5A-06-06, L5A-06-07 & L5A-06-08 | AGRICULTURE INSURANCE COMPANY OF INDIA LIMITED | Rated | Metered | Rack | Uncaged | No of Racks | 6 | 6 | 0 | 6 |  | 21666.6667 | Rated | KVA | 45 | 26.34 | 18.66 |  | #REF! | #REF! | 5.3492 | 0 | 0 | Metered | 1 | Fixed | 14.516 | 3979.84 | No of Seats | No of Seats | 1 | 1 | 0 | 1 |  | 8333.3333 | 130000 | 0 | 57771.3574 | 8333.3333 |  | 196104.6908 |  | 721005172 |  |  |  |  | 32684.1151 | #REF! | #REF! | #REF! | #REF! | 187771.3574 | 130000 | 57771.3574 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5A-07-03 | AGRICULTURE INSURANCE COMPANY OF INDIA LIMITED | Rated | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 21666.6667 | Rated | KVA | 3 | 8.32 | -5.32 |  | 0 | #REF! | 0.19746 | 5.32 | 0 | Metered | 1 | Fixed | 14.516 | 146.91 |  |  |  |  | 0 |  |  |  | 21666.6667 | 0 | 2132.5456 | 0 |  | 23799.2122 |  | 121001567 |  |  |  |  | 23799.2122 | #REF! | #REF! | #REF! | #REF! | 23799.2122 | 21666.6667 | 2132.5456 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5B-10-15, L5B-10-16, L5B-10-17, L5B-10-18, L5B-11-15 & L5B-11-16 | AGRICULTURE INSURANCE COMPANY OF INDIA LIMITED | Rated | Metered | Rack | Uncaged | No of Racks | 6 | 6 | 0 | 6 |  | 21666.6667 | Rated | KVA | 50 | 43.1 | 6.9 |  | #REF! | #REF! | 3.2057 | 0 | 0 | Metered | 1 | Fixed | 14.516 | 2385.03 | No of Seats | No of Seats | 1 | 1 | 0 | 1 |  | 8333.3333 | 130000 | 0 | 34621.0955 | 8333.3333 | 0 | 172954.4288 |  | 721004381, 721004451 & 721004508 |  |  |  |  | 28825.7381 | #REF! | #REF! | #REF! | #REF! | 164621.0955 | 130000 | 34621.0955 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5A-05-08, L5A-05-09 & L5A-05-10 | DENSO INTERNATIONAL INDIA PVT LTD | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  | 44722.2222 | Rated | KVA | 6 | 6 | 0 |  | 0 | #REF! | 1.87 | 0 | 7500 | Bundled | [8 empty] | 0 |  |  |  | 44722.2222 | 0 | 0 | 0 | 22916.6667 | 67638.8889 |  | Renewal |  |  |  |  | 67638.8889 | #REF! | #REF! | #REF! | #REF! | 44722.2222 | #REF! | #REF! | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L5 | L5B-01-03 & L5B-01-04 | BHARAT SANCHAR NIGAM LIMITED-HOSTING | Rated | Bundled | Rack | Uncaged | No of Racks | 2 | 2 | 0 | 2 |  | 50000 | Rated | KVA | 6 | 4.68 | 1.32 |  | #REF! | #REF! | 0.93 | 0 | 8166.6667 | Bundled | [8 empty] | 0 |  |  |  | 100000 | 0 | 0 | 0 | 10000 | 110000 |  | 721005561 |  |  |  |  | 55000 | #REF! | #REF! | #REF! | #REF! | 100000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L6 | L6-B-33 | STG SOFTWARE SOLUTION PRIVATE LIMITED | Rated | Bundled | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  |  | Rated | KVA | 12 | 7.31 | 4.69 |  | #REF! | #REF! | 6.3907 |  |  | Bundled |  |  |  | 4601.3 | [30 empty] | #REF! | [5 empty] | #REF!
L5 | L5A-01-10 | PEERCAST TELECOM INDIA PRIVATE LIMITED | Subscribed | Metered | Rack | Uncaged | No of Racks | 1 | 1 | 0 | 1 |  |  | Subscribed | KW | 3 | 1.0708 | 1.9292 |  | 1.9292 | 3 | 1.0708 | 0 |  | Metered | 1 | Fixed |  | 770.95 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | [6 empty] | 0 | 0 | #REF! |  |  | 0 | 0 | 0 | #REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | 3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
L7 | L7-F-18 | DELACON TECH SOLUTIONS PRIVATE LIMITED | Rated | Bundled | U space | Uncaged | U Space | 6 | 6 | 0 | 6 |  |  | Rated | KVA | 1.5 | 2.1 | -0.6 |  | 0 | #REF! |  | 0.6
L6 | L6-F-24 | REISNET BROADBAND PRIVATE LIMITED ( 5U TO 8U) | Rated | Bundled | U space | Uncaged | U Space | 4 | 4 | 0 | 4 |  |  | Rated | KVA | 1 | 0.3 | 0.7 |  | #REF! | #REF! |  | 0 |  | Bundled | [34 empty] | #REF! |  | #REF! |  |  |  | #REF!
L1 | NOI-TB-L1-A-15 TO NOI-TB-L1-A-17 | ACRO ENGINEERING | Subscribed | Metered | Rack | Uncaged | Racks | 3 | 3 | 0 | 3 |  | 474999 | Subscribed | KW | 27 | 0 | 27 |  | 27 | 27 | 0 | 0 |  | Bundal Metered |  |  |  | 0 | [44 empty] | Noida -02
Note on H3: Sreejith G: Formula added
Note on O3: Sreejith G: Formula
Note on Z3: Sreejith G: Formula
Note on N4: Mayank: RFP is for 6 Years
Note on AQ4: Mayank: 20 Mb Internet link
Note on Q5: 8257: 6 KVA + 2 KVA
Note on AQ5: 8257: Additional 2 KVA + 2 Nos of Safe vault + 9 Nos of ECC
Note on AQ10: Mayank: 5 Nos of FCC
Note on Q11: Mayank Jain: 500 W
Note on I17: Mayank: PO 1 for 5 Racks PO 2 for 1 Rack
Note on Q17: Mayank Jain: 6 Rack with 36 KVA + Addi 48.65
Note on Q18: Mayank: 1 KVA + 2 KVA additional
Note on AQ24: Mayank: 50 Mbps internet link
Note on I25: Mayank: OCM Rack @ 750000 OVM Rack @ 320000 Rack @ 225000
Note on N25: Mayank: OCM Rack @ 750000 OVM Rack @ 320000 Rack @ 225000
Note on AQ25: Mayank: 50 Mbps internet link
Note on AQ29: Mayank: RHS + Fiber Cross Connect
Note on AQ30: Mayank: Fiber cross connect for ISP & Google - 2 Nos
Note on AQ35: Mayank Jain: 6 FCC + SH + 100 ILL
Note on AQ37: Mayank: RHS
Note on AQ38: Mayank: 20 MB + 32 Extra IP
Note on AQ39: 8257: 1 No of Ethernet cross connect + 1 No of Fiber cross connect
Note on Q40: Mayank: 7.5 KW per Rack
Note on I43: Mayank: 1 Rack - 6 KVA 1 Rack - 3 KVA 1 Rack - 0 KVA
Note on N43: Mayank: Rs 860000 for 1 Rack - 6 KVA Rs 550000 for 1 Rack - 3 KVA Rs 200000 for 1 Rack - 0 KVA
Note on Q43: Mayank: 6 KVA + 3 KVA +3KVA +3 KVA ADDITIONAL
Note on AQ43: Mayank: RHS + Safe vault space + Tape rotaion + 3rd rack space
Note on AQ44: Mayank: 4 Nos of Fiber Cross Connect
Note on AQ46: Mayank: 20 MB + 32 Extra IP

## Noida-02
Floor | Floor / Module | Customer Name | RHS/SH | Sitting Space (Subscription) | Power Subscription Model (Rated/Subscribed) | Power Usage Model (Bundled / Metered) | Subscription Mode | Caged /Uncaged | UoM | Subscription | In Use | Yet to be given/ | Billed | Reserved Capacity if any (Non-Billable) | Per Unit rate (MRC) | Subscription Model | UoM | Total Capacity Purchased | Capacity in Use | Capacity to be given | Reserved Capacity if any | Subscribed Capacity to be given in KW | "Allocated" Capacity in KW (for KVA subscribed customer 50% diversity is used to make kW ) | DC NW Infra | Billable Additional Capacity | Additional Capacity Charges (MRC) | Usage Model | Multiplier | Uit rate Model (Fixed/Variable) | Unit Rate (per KW-HR) | No Of Units (KW-HR/ Month | Subscription Model | UoM | Subscription | In Use | Yet to be given | Billed | Reserved Capacity if any | Per Unit rate | Space revenue including capacity | Additional Capacity Revenue | Power Usage revenue | Seating Space | Any Other Items | Total Revenue | Billing Frequency | Sales Order ref No | Contract Start Date | Term of Contract (No of Years) | Current Exiry Date | Remarks if any | Avg revenue /Rack /Month | Avg revenue /KW /Month | Net Revenue / Resvd KW | Proj Net Revenue / Resvd KW | Sold Net Revenue / Resvd KW | Total Rev (Cap + Power) | Capacity Revenue | Power Revenue | Cost of Power @ Act Usage | Proj Cost of Power @ Reserv Cap | Cost of Power @ Design Use | Net Rev Total | Target Capacity Revenue | Capacity Surplus/Leakage | Power Surplus/Leakage | Contribution to Target | KW | Power Surplus/Leakage | Capacity Surplus/Leakage | Total Surplus/Leakage | Power Surplus/Leakage / KW | Capacity Surplus/Leakage / KW | Total Surplus/Leakage / KW
L5 | NOI-TB-L1-A-03 TO NOI-TB-L1-A-13 NOI-TB-L1-B-01 TO NOI-TB-L1-B-08 NOI-TB-L1-B-11 TO NOI-TB-L1-B-13 | Cloude flare | YES |  | Subscribed | Metered | Space | Caged | Sq Ft | 560 | 560 | 0 | 560 |  | 511700 | Subscribed | KW | 216 | 88.3363 | 127.6637 |  | 127.6637 | 216 | 88.3363 | 0 |  | Metered |  |  |  | 59362
L5 | NOI-TB-L1-C-03 TO NOI-TB-L1-C-07 NOI-TB-L1-D-03 TO NOI-TB-L1-D-07 | Zscaler | YES |  | Subscribed | Metered | Space | Caged | Sq Ft | 256 | 256 | 0 | 256 |  | 767000 | Subscribed | KW | 100 | 13.4717 | 86.5283 |  | 86.5283 | 100 | 13.4717 | 0 |  | Metered |  |  |  | 9053
| Optical Cage | EDGE NETWORK SERVICES LIMITED | YES |  | Subscribed | Metered | Space | Caged | Sq Ft | 432 | 288 | 144 | 288 |  |  | Subscribed | KW | 72 | 0 | 72 |  | 72 | 72 | 0 | 0 |  | Metered |  |  |  | 0
L5 | IP CAGE | EDGE NETWORK SERVICES LIMITED | YES |  | Subscribed | Metered | Space | Caged | Sq Ft | 5612 | 0 | 5612 | 0 |  | 2769200 | Subscribed | KW | 578 | 583.6604 | -5.6604 |  | 0 | 578 | 583.6604 | 5.6604 |  | Metered |  |  |  | 392219.77
| NOI-TB-L1-B-15 TO NOI-TB-L1-B-16 | ONEXTEL | YES |  | Subscribed | Metered | Rack | Uncaged | Racks | 2 | 2 | 0 | 2 |  | 205833 | Subscribed | KW | 24 | 10.0521 | 13.9479 |  | 13.9479 | 24 | 10.0521 | 0 |  | Metered |  |  |  | 6755
| Total of 1st Floor | [16 empty] | 990 | 695.5205 |  |  | 300.1399 | 990 | 695.5205
[6 empty] | Rack | 1 |  | Rack count | 2
[6 empty] | Space | 4 |  | Racks in Space | 326.6667
[6 empty] | U space | 0 |  | U space | 0
[9 empty] | Total | 328.6667
| L2 FLOOR | OCI | YES |  | Subscribed | Metered | Rack | Uncaged | Racks | 319 | 53 | 266 | 53 |  |  | Subscribed | KW | 2160 | 360.5685 | 1799.4315 |  | 1799.4315 | 2160 | 360.5685 | 0 |  | Metered |  |  |  | 242302
| Total of 2nd Floor | [16 empty] | 2160 | 360.5685 |  |  | 1799.4315 | 2160 | 360.5685
[6 empty] | Rack | 1 |  | Rack count | 319
[6 empty] | Space | 0 |  | Racks in Space | 0
[6 empty] | U space | 0 |  | U space | 0
[9 empty] | Total | 319
| Total of 8th Floor | [16 empty] | 87 | 43.2188 |  |  | 43.7812 | 87 | 43.2188
L5 | Server HALL L8 | Fastly | YES |  | Subscribed | Metered | Space | Caged | Sq Ft | 280 | 280 | 0 | 280 |  | 725000 | Subscribed | KW | 30 | 22.5923 | 7.4077 |  | 7.4077 | 30 | 22.5923 | 0 |  | Metered |  |  |  | 15182
L5 | NOI02 -TB-L8 -A-20 NOI02 -TB-L8 -A-21 | Chi Network | YES |  | Subscribed | Metered | Rack | Uncaged | Rack | 2 | 2 | 0 | 2 |  | 26666 | Subscribed | KW | 12 | 3.1131 | 8.8869 |  | 8.8869 | 12 | 3.1131 | 0 |  | Metered |  |  |  | 2092
| NOI02 -TB-L8 -B-19 NOI02 -TB-L8 -B-23 | ACRO ENGINEERING | YES |  | Subscribed | Bundled | Rack | Uncaged | Rack | 5 | 5 | 0 | 5 |  | 157500 | Subscribed | KW | 45 | 17.5134 | 27.4866 |  | 27.4866 | 45 | 17.5134 | 0 |  | Bundled |  |  |  | 11769
[6 empty] | Rack | 2 |  | Rack count | 7
[6 empty] | Space | 1 |  | Racks in Space | 13.3333
[6 empty] | U space | 0 |  | U space | 0
[9 empty] | Total | 20.3333
Note on J1: Sreejith G: Formula added
Note on Q1: Sreejith G: Formula
Note on AB1: Sreejith G: Formula
Note on AS2: Mayank: RHS
Note on AS3: Mayank: 5.93 KVA additional Power + 2 ECC
Note on AS19: Mayank: RHS
Note on AS20: Mayank: 5.93 KVA additional Power + 2 ECC